## LOAD DETAILS
I.T.I PROJECT-OPT-4-LOAD DETAIL
Date: 30-12-22
Sr. No. | AREA DESCRIPTION | Connected Load | Diversity Factor | MAX. DEMAND LOAD | REMARK
A | GENERAL LIGHTING
1 | WORKSHOP | 9.6 | 0.8 | 7.68
2 | LAB AND CLASSROOM AREA | 16.8 | 0.8 | 13.44
|  | 26.4 |  | 21.12
B | POWER AND AC LOAD
1 | LAB AND CLASSROOM AREA | 32 | 0.8 | 25.6
|  | 32 |  | 25.6
C | UPS LOAD
1 | LAB AND CLASSROOM AREA | 12 | 0.8 | 9.6
|  | 12 |  | 9.6
C | OTHER UTILITY LOAD
1 | MACHINE LOADS-1-63A SOCKET | 7.5 | 0.7 | 5.25
2 | MACHINE LOADS-2-63A SOCKET | 7.5 | 0.7 | 5.25
3 | MACHINE LOADS-3-63A SOCKET | 7.5 | 0.7 | 5.25
4 | MACHINE LOADS-4-63A SOCKET | 7.5 | 0.7 | 5.25
5 | MACHINE LOADS-5-63A SOCKET | 7.5 | 0.7 | 5.25
6 | MACHINE LOADS-6-63A SOCKET | 7.5 | 0.7 | 5.25
7 | MACHINE LOADS-7-63A SOCKET | 7.5 | 0.7 | 5.25
8 | MACHINE LOADS-8-32A SOCKET | 5 | 0.7 | 3.5
9 | MACHINE LOADS-9-32A SOCKET | 5 | 0.7 | 3.5
| TOTAL LOAD | 117.9 |  | 89.57
CONNECTED LOAD FOR THE BUILDING |  |  |  | 117.9
DEMAND LOAD FOR THE BUILDING |  |  |  | 89.57

## DB DETAILS
DB DETAIL FOR I.T.I PROJECTS
I.T.I PROJECT-LIGHT DB(B)
6WAY TPN DB |  | INCOMER - 40A-4P MCB |  | 3NOS-32 AMP-DP-RCCB/ELCB
SUBMAIN | 4CX10SQMM CU PVC CABLE
CKT NO. | CABLE WIRE SIZE | MCB FEEDER | LOCATION | LOADS IN WATT
|  |  |  | R | Y | B
B1 | 2X1.5SQMM WIRE+1X1.5SQMM | 6AMP | LIGHT CIRCUIT | 800
B2 | 2X1.5SQMM WIRE+1X1.5SQMM | 6AMP | LIGHT CIRCUIT |  | 800
B3 | 2X1.5SQMM WIRE+1X1.5SQMM | 6AMP | LIGHT CIRCUIT |  |  | 800
B4 | 2X1.5SQMM WIRE+1X1.5SQMM | 6AMP | LIGHT CIRCUIT | 800
B5 | 2X1.5SQMM WIRE+1X1.5SQMM | 6AMP | LIGHT CIRCUIT |  | 800
B6 | 2X1.5SQMM WIRE+1X1.5SQMM | 6AMP | LIGHT CIRCUIT |  |  | 800
B7 | 2X1.5SQMM WIRE+1X1.5SQMM | 6AMP | LIGHT CIRCUIT | 800
B8 | 2X1.5SQMM WIRE+1X1.5SQMM | 6AMP | LIGHT CIRCUIT |  | 800
B9 | 2X1.5SQMM WIRE+1X1.5SQMM | 6AMP | LIGHT CIRCUIT |  |  | 800
B10 | SPARE
B11 | SPARE
B12 | SPARE
TOTAL LOAD/PHASE |  |  |  | 2400 | 2400 | 2400
TOTAL LIGHT LOAD |  |  |  | 7.2
I.T.I PROJECT-LIGHT DB(C)
8WAY TPN DB |  | INCOMER - 40A-4P MCB |  | 3NOS-32 AMP-DP-RCCB/ELCB
SUBMAIN | 4CX10SQMM CU PVC CABLE
CKT NO. | CABLE WIRE SIZE | MCB FEEDER | LOCATION | LOADS IN WATT
|  |  |  | R | Y | B
C1 | 2X1.5SQMM WIRE+1X1.5SQMM | 6AMP | LIGHT CIRCUIT | 800
C2 | 2X1.5SQMM WIRE+1X1.5SQMM | 6AMP | LIGHT CIRCUIT |  | 800
C3 | 2X1.5SQMM WIRE+1X1.5SQMM | 6AMP | LIGHT CIRCUIT |  |  | 800
C4 | 2X1.5SQMM WIRE+1X1.5SQMM | 6AMP | LIGHT CIRCUIT | 800
C5 | 2X1.5SQMM WIRE+1X1.5SQMM | 6AMP | LIGHT CIRCUIT |  | 800
C6 | 2X1.5SQMM WIRE+1X1.5SQMM | 6AMP | LIGHT CIRCUIT |  |  | 800
C7 | 2X1.5SQMM WIRE+1X1.5SQMM | 6AMP | LIGHT CIRCUIT | 800
C8 | 2X1.5SQMM WIRE+1X1.5SQMM | 6AMP | LIGHT CIRCUIT |  | 800
C9 | 2X1.5SQMM WIRE+1X1.5SQMM | 6AMP | LIGHT CIRCUIT |  |  | 800
C10 | 2X1.5SQMM WIRE+1X1.5SQMM | 6AMP | LIGHT CIRCUIT | 800
C11 | 2X1.5SQMM WIRE+1X1.5SQMM | 6AMP | LIGHT CIRCUIT |  | 800
C12 | 2X1.5SQMM WIRE+1X1.5SQMM | 6AMP | LIGHT CIRCUIT |  |  | 800
C13 | SPARE
C14 | SPARE
C15 | SPARE
C16 | SPARE
C17 | SPARE
C18 | SPARE
TOTAL LOAD/PHASE |  |  |  | 3200 | 3200 | 3200
TOTAL LIGHT LOAD |  |  |  | 9.6
I.T.I PROJECT-LIGHT DB(A)
6WAY TPN DB |  | INCOMER - 40A-4P MCB |  | 3NOS-32 AMP-DP-RCCB/ELCB
SUBMAIN | 4CX10SQMM CU PVC CABLE
CKT NO. | CABLE WIRE SIZE | MCB FEEDER | LOCATION | LOADS IN WATT
|  |  |  | R | Y | B
A1 | 2X1.5SQMM WIRE+1X1.5SQMM | 6AMP | LIGHT CIRCUIT | 800
A2 | 2X1.5SQMM WIRE+1X1.5SQMM | 6AMP | LIGHT CIRCUIT |  | 800
A3 | 2X1.5SQMM WIRE+1X1.5SQMM | 6AMP | LIGHT CIRCUIT |  |  | 800
A4 | 4C X 6SQMM PVC CABLE | 10AMP | FLOOD LIGHTS | 800
A5 | 4C X 6SQMM PVC CABLE | 10AMP | FLOOD LIGHTS |  | 800
A6 | 2X1.5SQMM WIRE+1X1.5SQMM | 6AMP | LIGHT CIRCUIT |  |  | 800
A7 | 2X1.5SQMM WIRE+1X1.5SQMM | 6AMP | LIGHT CIRCUIT | 800
A8 | SPARE
A9 | SPARE
A10 | SPARE
A11 | SPARE
A12 | SPARE
TOTAL LOAD/PHASE |  |  |  | 2400 | 1600 | 1600
TOTAL LIGHT LOAD |  |  |  | 5.6
I.T.I PROJECT-LIGHT DB(F)
6WAY TPN DB |  | INCOMER - 40A-4P MCB |  | 3NOS-32 AMP-DP-RCCB/ELCB
SUBMAIN | 4CX10SQMM CU PVC CABLE
CKT NO. | CABLE WIRE SIZE | MCB FEEDER | LOCATION | LOADS IN WATT
|  |  |  | R | Y | B
F1 | 2X1.5SQMM WIRE+1X1.5SQMM | 6AMP | LIGHT CIRCUIT | 800
F2 | 2X1.5SQMM WIRE+1X1.5SQMM | 6AMP | LIGHT CIRCUIT |  | 800
F3 | 2X1.5SQMM WIRE+1X1.5SQMM | 6AMP | LIGHT CIRCUIT |  |  | 800
F4 | 4C X 6SQMM PVC CABLE | 10AMP | FLOOD LIGHTS | 800
F5 | 4C X 6SQMM PVC CABLE | 10AMP | FLOOD LIGHTS |  | 800
F6 | SPARE
F7 | SPARE
F8 | SPARE
F9 | SPARE
F10 | SPARE
F11 | SPARE
F12 | SPARE
TOTAL LOAD/PHASE |  |  |  | 1600 | 1600 | 800
TOTAL LIGHT LOAD |  |  |  | 4
I.T.I PROJECT-POWER DB (D)
6WAY TPN DB |  | INCOMER - 63A-4P MCB |  | 3NOS-40 AMP-DP-RCCB/ELCB
SUBMAIN | 3CX16+1X10 Sqmm CU CABLE
CKT NO. | CABLE WIRE SIZE | MCB FEEDER | LOCATION | LOADS IN WATT
|  |  |  | R | Y | B
D1 | 2X4SQMM WIRE+1X2.5SQMM | 16AMP | 1X16A SOCKET | 1000
D2 | 2X4SQMM WIRE+1X2.5SQMM | 16AMP | 1X16A SOCKET |  | 1000
D3 | 2X4SQMM WIRE+1X2.5SQMM | 16AMP | 1X16A SOCKET |  |  | 1000
D4 | 2X4SQMM WIRE+1X2.5SQMM | 16AMP | 1X16A SOCKET | 1000
D5 | 2X6SQMM WIRE+1X4.0SQMM | 20AMP | AC SOCKET |  | 2000
D6 | 2X6SQMM WIRE+1X4.0SQMM | 20AMP | AC SOCKET |  |  | 2000
D7 | 2X6SQMM WIRE+1X4.0SQMM | 20AMP | AC SOCKET | 2000
D8 | 2X6SQMM WIRE+1X4.0SQMM | 20AMP | AC SOCKET |  | 2000
D9 | 2X6SQMM WIRE+1X4.0SQMM | 20AMP | AC SOCKET |  |  | 2000
D10 | SPARE
D11 | SPARE
D12 | SPARE
TOTAL LOAD/PHASE |  |  |  | 4000 | 5000 | 5000
TOTAL LOAD OF DB |  |  |  | 14
I.T.I PROJECT-POWER DB (E)
8WAY TPN DB |  | INCOMER - 63A-4P MCB |  | 3NOS-40 AMP-DP-RCCB/ELCB
SUBMAIN | 3CX16+1X10 Sqmm CU CABLE
CKT NO. | CABLE WIRE SIZE | MCB FEEDER | LOCATION | LOADS IN WATT
|  |  |  | R | Y | B
E1 | 2X4SQMM WIRE+1X2.5SQMM | 16AMP | 1X16A SOCKET | 1000
E2 | 2X4SQMM WIRE+1X2.5SQMM | 16AMP | 1X16A SOCKET |  | 1000
E3 | 2X4SQMM WIRE+1X2.5SQMM | 16AMP | 1X16A SOCKET |  |  | 1000
E4 | 2X4SQMM WIRE+1X2.5SQMM | 16AMP | 1X16A SOCKET | 1000
E5 | 2X4SQMM WIRE+1X2.5SQMM | 16AMP | 1X16A SOCKET |  | 1000
E6 | 2X4SQMM WIRE+1X2.5SQMM | 16AMP | 1X16A SOCKET |  |  | 1000
E7 | 2X6SQMM WIRE+1X4.0SQMM | 20AMP | AC SOCKET | 2000
E8 | 2X6SQMM WIRE+1X4.0SQMM | 20AMP | AC SOCKET |  | 2000
E9 | 2X6SQMM WIRE+1X4.0SQMM | 20AMP | AC SOCKET |  |  | 2000
E10 | 2X6SQMM WIRE+1X4.0SQMM | 20AMP | AC SOCKET | 2000
E11 | 2X6SQMM WIRE+1X4.0SQMM | 20AMP | AC SOCKET |  | 2000
E12 | 2X6SQMM WIRE+1X4.0SQMM | 20AMP | AC SOCKET |  |  | 2000
E13 | SPARE
E14 | SPARE
E15 | SPARE
E16 | SPARE
E17 | SPARE
E18 | SPARE
TOTAL LOAD/PHASE |  |  |  | 6000 | 6000 | 6000
TOTAL LOAD OF DB |  |  |  | 18
I.T.I UPS DB (U)
8WAY V-TPN DB |  | INCOMER - 40A-4P MCB
SUBMAIN | 4CX6 Sqmm CU CABLE
CKT NO. | CABLE WIRE SIZE | MCB FEEDER | LOCATION | LOADS IN WATT
|  |  |  | R | Y | B
U1 | 2X1.5SQMM WIRE+1X1.5SQMM | 6AMP | 6/16A SOCKETS | 800
U2 | 2X1.5SQMM WIRE+1X1.5SQMM | 6AMP | 6/16A SOCKETS |  | 800
U3 | 2X1.5SQMM WIRE+1X1.5SQMM | 6AMP | 6/16A SOCKETS |  |  | 800
U4 | 2X1.5SQMM WIRE+1X1.5SQMM | 6AMP | 6/16A SOCKETS | 800
U5 | 2X1.5SQMM WIRE+1X1.5SQMM | 6AMP | 6/16A SOCKETS |  | 800
U6 | 2X1.5SQMM WIRE+1X1.5SQMM | 6AMP | 6/16A SOCKETS |  |  | 800
U7 | 2X1.5SQMM WIRE+1X1.5SQMM | 6AMP | 6/16A SOCKETS | 800
U8 | 2X1.5SQMM WIRE+1X1.5SQMM | 6AMP | 6/16A SOCKETS |  | 800
U9 | 2X1.5SQMM WIRE+1X1.5SQMM | 6AMP | 6/16A SOCKETS |  |  | 800
U10 | 2X1.5SQMM WIRE+1X1.5SQMM | 6AMP | 6/16A SOCKETS | 800
U11 | 2X1.5SQMM WIRE+1X1.5SQMM | 6AMP | 6/16A SOCKETS |  | 800
U12 | 2X1.5SQMM WIRE+1X1.5SQMM | 6AMP | 6/16A SOCKETS |  |  | 800
U13 | 2X1.5SQMM WIRE+1X1.5SQMM | 6AMP | 6/16A SOCKETS | 800
U14 | 2X1.5SQMM WIRE+1X1.5SQMM | 6AMP | 6/16A SOCKETS |  | 800
U15 | 2X1.5SQMM WIRE+1X1.5SQMM | 6AMP | 6/16A SOCKETS |  |  | 800
U16 | SPARE
U17 | SPARE
U18 | SPARE
TOTAL LOAD/PHASE |  |  |  | 4000 | 4000 | 4000
TOTAL LOAD L1 |  |  |  | 12